October 17, 2007

Bob Gallagher

Re:1550 Felta Rd.

On October 13, 2007 we pulled the existing pump out of the old well and set it in the new well. A test was run for 12 hours into the concrete tank.

The well production reported is what the existing pump will produce under normal operating conditions. If a larger pump were installed, the well would supply more GPM’s than this test showed.

The following are the particulars regarding the well and pump installed.

Well depth  			240’

Pump installed			1 HP 10P submersible

Casing 			5” PVC

Static water level		155’ 0”

Pumping level at 7.8 GPM	155’ 2”

Drawdown			0’ 2”

Length of test			12 hours

Date of installation		6/07

Pump setting			on 215’ 1” SCH 80 PVC

If you have any questions please feel free to give me a call.

Thank you,

Robert L. Plum